Permit Application #2004.3 Annual Marine Fuel Transfer Permit

# Tacoma Fire Department
Fire Prevention Division 253.591.5740
FAX Number 253.594.7943 
3471 S. 35th St. Tacoma, WA 98409
www.tacomafiredepartment.org

Submit Paper Work by Hand, Mail, Fax, E-mail to: TFDHMO@cityoftacoma.org

To be completed by the Permit Applicant  (type in the grey box or print out and complete)

| ### Business Information |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Date: |  |  |  | Federal Tax ID: |  |  |  |
| Business Name: |  |  |  | UBI: |  |  |  |
| Address: | Street |  |  | City |  | State | Zip |
| Site Address: | (if different from above) |  |  |  |  |  |  |
| Contact Name: |  |  |  |  |  |  |  |
| Phone: | ( ) |  |  | Alternate Phone/Cell: ( ) |  |  |  |
| E-mail Address: |  |  |  |  |  |  |  |
| City of Tacoma Business License: |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |
| ### Please include a check made payable to the CITY OF TACOMA TREASURER, or request an invoice. |  |  |  |  |  |  |  |
| Check this box to have the applicant invoiced for this permit. |  |  |  |  |  |  |  |
| ### FPB OFFICIAL USE ONLY |  |  |  |  |  |  |  |
| Approved By: |  |  | Date: |  |  |  |  |
| Denied: | Reason for Denial: |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |
| Permit Number: |  |  |  |  |  |  |  |
| Permit Fees: | Date Received: | Receipt Number: |  |  | Check Number: |  |  |

See attached documentation for description of conditions that must be met prior to the issuance of this permit.

- Marine Terminal -

# Tacoma Fire Department

PERMIT CONDITIONS:  #2004.3 Annual Marine Fuel Transfer Permit

All of the following conditions must be met prior to the issuance of a permit.

# 1. Timelines

- An annual permit is required prior to commencement of fueling operations.  The anniversary date will be established with the issue of the first permit.

# 2. Regulatory references

- International Fire Code Ch 22, 34 & 46

- National Fire Protection Association 30A

- State of Washington WAC 173-180

# 3. Required Submittals

- Tacoma Fire Department Permit Application

- City of Tacoma business license (provide on application)

- Site Plan

- Company spill response plan

# 4. Inspection requirements

- Annual inspection of premises

# 5. Requirements

- Ability to clean up a spill of at least 25 gallons with resources on site.

- 200 feet of boom on standby, along with oil spill sorbent materials, shovels, buckets, containers and protective clothing.

- Post oil spill notification numbers and oil spill response contractor number in a conspicuous and obvious place.

- Posting of Warning signs:

1.     Signs shall be prominently displayed at the face of each wharf, pier 
        or float.

2.     Signs shall have letters not less than 3 inches in height on a 
        background of contrasting color with the following statements:

WARNING

NO SMOKING-STOP ENGINE WHILE FUELING

SHUT OFF ELECTRICITY

DO NOT START ENGINE UNTIL AFTER BELOW DECK

SPACES ARE VENTILATED

3.  No Smoking signs shall have letters not less than 4 inches in height on 
                a background of contrasting color stating:

NO SMOKING WITHIN 50 FEET

4.   Fire Extinguishers with a Minimum rating of 20BC

- Shall be installed as indicated:

1.    One on each float

2.    One on the pier or wharf within 25 feet of the head of the gangway to 
       the float, unless the office is within 25 feet of the gangway or is on 
       the float and an extinguisher is provided.

- Sources of ignition: Construction, maintenance, repair and reconditioning work involving the use of open flames, arcs or spark producing devices shall not be performed at marine motor fuel dispensing sites within 50 of dispensing facilities.

- Fueling is not allowed when the items above are being conducted.

- LPG cylinders shall not be filled at marine motor fuel dispensing facilities unless approved.

- Rubbish containers shall be metal containers with tight fitting or self closing metal lids.

- Dispensing of Class 1 or Class II shall be done with an approved automatic closing nozzle without a latch open device.

- Hoses used for dispensing fuel shall be racked, reeled or otherwise protected from mechanical damage.

- Dispensing facilities shall have an attendant on duty that is fully aware of the operation, mechanics and hazards inherent to fueling whenever the facility is open for business.