Permit Application #2005.1 Application of Flammable Finishes

# Tacoma Fire Department
Fire Prevention Division 253.591.5740
FAX Number 253.594.7943 
3471 S. 35th St. Tacoma, WA 98409
www.tacomafiredepartment.org

Submit Paper Work by Hand, Mail, Fax, E-mail to: TFDHMO@cityoftacoma.org

To be completed by the Permit Applicant (type in the grey box or print out and complete)

| ### Business Information |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: |  |  |  |  |  | Federal Tax ID: |  |  |  |  |  |
| Business Name: |  |  |  |  |  | UBI: |  |  |  |  |  |
| Address: | Street |  |  |  |  | City |  |  | State |  | Zip |
| Site Address: | (if different from above) |  |  |  |  |  |  |  |  |  |  |
| Contact Name: |  |  |  |  |  |  |  |  |  |  |  |
| Phone: | ( ) |  |  |  |  | Alternate Phone/Cell: ( ) |  |  |  |  |  |
| E-mail Address: |  |  |  |  |  |  |  |  |  |  |  |
| City of Tacoma Business License:; PSAPCA Registry Number:. RCRA Number:. Comments:. |
| ### Please include a check made payable to the CITY OF TACOMA TREASURER, or request an invoice. |  |  |  |  |  |  |  |  |  |  |  |
| Check this box to have the applicant invoiced for this permit. |  |  |  |  |  |  |  |  |  |  |  |
| ### FPB OFFICIAL USE ONLY |  |  |  |  |  |  |  |  |  |  |  |
| Approved By: |  |  |  |  | Date: |  |  |  |  |  |  |
| Denied: | Reason for Denial: |  |  |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |
| Permit Number: |  |  |  |  |  |  |  |  |  |  |  |
| Permit Fees: | Date Received: |  |  | Receipt Number: |  |  |  | Check Number: |  |  |  |
| Type of Operation |  | Full: | Limited: |  |  |  | Powder Coating: |  |  | Dip Coating: |  |

See attached documentation for description of conditions that must be met prior to the issuance of this permit.

- Spray Finishing -

# Tacoma Fire Department

PERMIT CONDITIONS: #2005.1 – Application of Flammable Finishes

Scope:   This permit applies to the application of material coatings in which the material being applied is a flammable liquid, combustible liquid, combustible powder or flammable or combustible gel coating.

All of the following conditions must be met prior to the issuance of a permit.

# 1.   Time Lines

- Application shall be approved prior to commencement of spray operations.

# 2.   Regulatory References

a.    	NFPA Standard 33

b.    	International Fire Code Chapter 15

# 3.   Required Submittals

a.	Tacoma Fire Department permit application

b.   	City of Tacoma Business License (place on application)

c.   	Puget Sound Air Pollution Control Agency Registry Number (PSAPCA)

d.	Resource Conservation & Recovery Act Number (WA DOE) (If more than 220 pounds per month)

e.    	South Tacoma Ground Water Protection District. Permit (PCHD), if applicable

f.    	Fire Suppression System Certification

g.    	Installation Permit (For new spray booth) (COT)

# 4.   Inspection Requirements

- An inspection of the building, spray booth, and/or dip tanks shall be completed for final    
      approval.

- Compliance with regulatory statutes and standards

# 5.   Requirements

# Spray Finishing and Powder Coating Operations

- Proof of compliance with agencies requiring permits shall be met prior to permit being 
      issued by Tacoma Fire Department.

- Annual Spray Finishing Permit -Tacoma Fire Department

- If booth is in excess of 10% aggregate square feet, building is subject to occupancy type    
      revision by Building and Land Use Services.

- Fire suppression system currently certified

Ventilation

- Average air velocity at face of booth 100 LFM (gauge)

- Independent exhaust system through vertical stack

- Duct cleanout accessible and clean

- No elbows or bends to exceed 45 degrees

- No exposed belts, pulleys, or electric motors in duct work or booth

- Makeup air system operable

Ventilation Discharge

- 30 feet from property line

- 10 feet from doors and window

- 6 feet above roof

d.          10 feet above adjoining grade

Flammable Liquids

- Liquids exceeding 10 gallons must be stored in approved cabinet

- Maximum storage of Class I/II - 60 gallons

# Powder Coating Operations

a. 	Additional fire protection required:  Automated powder application equipment shall be

protected by the installation of an approved, supervised flame detection apparatus that shall react to the presence of flame within 0.5 second and shall accomplish the following:

1. Shut down of energy supplies to conveyor, ventilation, application, transfer and

powder collection equipment.

2. Close segregation dampers in associated ductwork to interrupt airflow from

application equipment to powder collectors.

3. Activation of an alarm that is audible throughout the powder coating room or   
    booth.

b. 	Cleaning – Vacuum sweeping equipment shall be of a type approved for use in hazardous locations.

c. 	Spark producing metals – Iron or spark producing metals shall be prevented from being

introduced to the powders being applied by magnetic separators or other approved means.

d. 	Grounding and bonding - Precautions shall be taken to minimize the possibility of ignition by static electrical sparks through static bonding and grounding. This includes powder transport, application equipment and powder recovery systems.

e. 	Ventilation – Exhaust ventilation shall be maintained at one-half (½) the minimum explosive concentration listed for the material being applied.

# Dipping Operations

a.  	Additional fire protection required: an approved automatic fire extinguishing system or dip-tank cover shall be provided for the following dip tanks:

1. Dip tanks less than 150 gallons in capacity or 10 square feet in liquid surface   
    area.

2. Dip tanks containing a liquid with a flash point below 110 degrees F and  
    having a capacity of more than 10 gallons and a liquid surface of more than 4   
    square feet.

b. 	Ventilation: Required ventilation systems shall be arranged so that the failure of any ventilating fan shall automatically stop the dipping conveyor system.

c. 	Conveyor interlock – dip tanks utilizing a conveyor belt system shall be arranged so that in the event of a fire the conveyor belt shall cease motion and the required tank drains shall open.

d. 	Portable fire extinguishers - Areas in the vicinity of dip tank operations shall be provided with PFEs suitable for flammable and combustible liquids as specified for extra (high) hazard occupancies.

# Contact the following organizations prior to conducting a spray operating business:

| Organization | Contact Information |
| --- | --- |
| City of Tacoma-Building and Land Use- BLUS 747 Market St. – 3rd floor Permits - Make appointment to review project with an engineer Permits required: Building Mechanical Electrical Ventilation Fire protection system | 253-591-5033 Website |
| City of Tacoma Fire Department- Permits required: Fire Protection System Annual Spray Painting | 253-591-5739 |
| Puget Sound Clean Air Permit required | 800-552-3565 Website |
| Washington State Office of Regulatory Assistance Permit required | 800-917-0043 Website |
| Washington State Department of Labor and Industries | 800-547-8367 Website |
| City of Tacoma-Waste Water Source Control | 253-591-5588 Website |
| City of Tacoma- Tax and License | 253-591-5252 Website |
| Tacoma Pierce County Health Department South Tacoma Ground Water area sites | 253-798-6429 Website |