Permit Application #2007.3  Special Hazardous Materials Permit

# Tacoma Fire Department
Fire Prevention Division 253.591.5740
FAX Number 253.594.7943 
3471 S. 35th St. Tacoma, WA 98409
www.tacomafiredepartment.org

Submit Paper Work by Hand, Mail, Fax, E-mail to: TFDHMO@cityoftacoma.org

To be completed by the Permit Applicant (type in the grey box or print out and complete)

| ### Business Information |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Date: |  |  |  | Federal Tax ID: |  |  |  |
| Business Name: |  |  |  | UBI: |  |  |  |
| Address: | Street: |  |  | City: |  | State: | Zip: |
| Site Address: | (if different from above) |  |  |  |  |  |  |
| Contact Name: |  |  |  |  |  |  |  |
| Phone: | ( ) |  |  | Alternate Phone/Cell: ( ) |  |  |  |
| E-mail Address: |  |  |  |  |  |  |  |
| City of Tacoma Business License: |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |
| ### Please include a check made payable to the CITY OF TACOMA TREASURER, or request an invoice. |  |  |  |  |  |  |  |
| Check this box to have applicant invoiced for this permit. |  |  |  |  |  |  |  |
| ### FPB OFFICIAL USE ONLY |  |  |  |  |  |  |  |
| Approved By: |  |  | Date: |  |  |  |  |
| Denied: | Reason for Denial: |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |
| Permit Number: |  |  |  |  |  |  |  |
| Permit Fees: | Date Received: | Receipt Number: |  |  | Check Number: |  |  |

See attached documentation for description of conditions that must be met prior to the issuance of this permit.

-Special Haz-Mat-

# Tacoma Fire Department

PERMIT CONDITIONS: #2007.3 Special Hazardous Material Permit

Scope:  The use or handling of hazardous materials in excess of the quantities listed in the attached table and not covered under an Annual Hazardous Materials Permit or Annual Marine Terminal Permit is subject to the conditions of this permit.

All of the following conditions must be met prior to the issuance of a permit.

# 1. Timelines

- Prior to conducting activity related to the scope of this permit, an approved permit shall be issued.

# 2. Regulatory References

- International Fire Code

- Hazardous Materials Quantity Table

# 3. Required Submittals

- Tacoma Fire Department Permit Application

- City of Tacoma business license (enter on permit)

- Site plan of facility

- Hazardous Material Inventory Sheet(s)

- Hazardous Materials Management Plan

- Accidental Spill and Release Contingency Plans

# 4.  Inspection Requirements

a.	Inspection and approval prior to issuance of permit

# 5. Requirements

- Increases in the amounts for each hazard class requires evaluation prior

to approval and are evaluated on a per case basis, may require additional  
                           fees

- Approved permit to remain on-site

- NFPA 704 Signs per MSDS must be visible from the street.

# Tacoma Fire Department

HAZARDOUS MATERIALS QUANTITY TABLE

Amounts of Hazardous Materials exceeding the following thresholds REQUIRE PERMITS

| TYPE OF MATERIAL | AMOUNT |
| --- | --- |
| UN Class 1 - Explosives Materials |  |
| Division 1.1 | 1 pound |
| Division 1.2 | 1 pound |
| Division 1.3 | 5 pounds |
| Division 1.4 | 50 pounds |
| Division 1.4G | 125 pounds |
| Division 1.5 | 1 pound |
| Division 1.6 | 1 pound |
| UN Class 2 - Gases |  |
| Flammable Gases |  |
| 1. Gaseous | 1000 cubic feet |
| 2. Liquefied (except propane) | 30 gallons |
| Toxic Gases | 810 cubic feet |
| Highly Toxic Gases | 20 cubic feet |
| Pyrophoric Gases | 50 cubic feet |
| UN Class 3 - Flammable Liquids |  |
| Flammable Liquids (UN Class 3) |  |
| Class 1A | 30 gallons |
| Class 1B and 1C | 120 gallons |
| Combustible Liquid (UN Class 3) |  |
| Class II | 120 gallons |
| Class IIIA | 330 gallons |
| Class IIIB | 13,200 gallons |
| UN Class 4 - Flammable Solids and Reactive Liquids and Solids |  |
| Flammable Solids | 125 pounds |
| Pyrophoric Materials |  |
| Liquid | 4 pounds |
| Solid | 4 pounds |
| Water Reactive – Liquids and Solids |  |
| Class 3 | 5 pounds |
| Class 2 | 50 pounds |
| Class 1 | No permit required. |
| Unstable (reactive) Materials – Liquids and Solids |  |
| Class 4 | 1 pounds |
| Class 3 | 5 pounds |
| Class 2 | 50 pounds |
| Class 1 | No permit required. |
| UN Class 5 - Oxidizers and Organic Peroxides |  |
| Oxidizing Materials – Gases |  |
| Gaseous | 1500 cubic feet |
| Liquefied | 15 gallons |
| Liquids and Solids |  |
| Class 4 | 1 pound |
| Class 3 | 10 pounds |
| Class 2 | 250 pounds |
| Class 1 | 4000 pounds |
| Organic Peroxides- Liquids and Solids |  |
| Class I | 5 pounds |
| Class II | 50 pounds |
| Class III | 125 pounds |
| Class IV | No permit required. |
| Class V | No permit required. |
| UN Class 6 - Toxic (poisonous) Materials |  |
| Toxic Materials |  |
| Liquids | 500 pounds |
| Solids | 500 pounds |
| Highly Toxic Materials |  |
| Liquids | 10 pounds |
| Solids | 10 pounds |
| UN Class 7 - Radioactive Materials | No Tacoma Fire Department permit is required: however, such materials may require State of Washington permits. |
| UN Class 8 - Corrosive Materials |  |
| Gases | 810 cubic feet |
| Liquids | 500 gallons |
| Solids | 5000 pounds |
| UN Class 9 – Miscellaneous Hazardous Materials | There are no Tacoma Fire Department permits required in this section. However, one may be required by the Tacoma - Pierce County Health Department or the State of Washington based on their threshold criteria. Check with these agencies for more information. |
| Anesthetic or noxious substances. |  |
| Elevated temperature materials. |  |
| Environmentally hazardous substances. |  |
| Marine pollutants. |  |
| Medical waste. |  |
| Hazardous waste, not in any of Classes 1 through 8. |  |
| Other regulated hazardous substance or object. |  |