Permit Application #2000.3  Underground Tank – Removal or Decommissioning - Commercial


To be completed by the Permit Applicant (type in the grey box or print out and complete)

# Tacoma Fire Department
Fire Prevention Division 253.591.5740
FAX Number 253.594.7943 
3471 S. 35th St. Tacoma, WA 98409
www.tacomafiredepartment.org

| ### Business Information |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date: |  |  |  |  | Projected Start Date: |  |  |  |
| Business Name: |  |  |  |  |  |  |  |  |
| Address: | Street |  |  | City |  |  | State | Zip |
| Site Address: | (if different from above) |  |  |  |  |  |  |  |
| Contact Name: |  |  |  |  |  |  |  |  |
| Phone: | ( ) |  |  |  | Alternate Phone/Cell: ( ) |  |  |  |
| E-mail Address: |  |  |  |  |  |  |  |  |
| City of Tacoma Business License:; Washington State Contractor License:; ICC UST Certification #. Comments:. |
| ### Please include a check made payable to the CITY OF TACOMA or request an invoice. |  |  |  |  |  |  |  |  |
| Check this box to have the applicant invoiced for the permit fee. |  |  |  |  |  |  |  |  |
| ### FPB OFFICIAL USE ONLY |  |  |  |  |  |  |  |  |
| Approved By: |  |  | Date: |  |  |  |  |  |
| Denied: | Reason for Denial: |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |
| Permit Number: |  |  |  |  |  |  |  |  |
| Permit Fees: | Date Received: | Receipt Number: |  |  |  | Check Number: |  |  |

See attached documentation for description of conditions that must be met prior to the issuance of this permit.

-Underground Tank-

# Tacoma Fire Department

PERMIT CONDITIONS: # 2000.3 Underground Tank Removal or Decommissioning - Commercial

All of the following conditions must be met prior to the issuance of a permit.

1.   Time Lines

- Applications to be submitted 14 days prior to projected removal or decommissioning date.

# 2.   Regulatory References

- International Fire Code (IFC)  Chapter 34

- NFPA Standard 30

- Washington State Department of Ecology UST Tank Closure

- WAC 173-360-385

- Tacoma Municipal Code 13.09

- South Tacoma Ground Water Protection District Reference map

# 3.   Required Submittals

- Tacoma Fire Department Permit Application

- City of Tacoma business license (enter on application)

- Washington State contractors license (enter on application)

- Tacoma Pierce County Health Department approval permit ( all tanks)

- ICC UST Certification

UPON COMPLETION SUBMIT A COPY OF:

- Washington State Dept. of Ecology 30 Day Notice - Form ECY020-95

- Washington State Dept. of Ecology  Form ECY-94

- Washington State Dept. of Ecology Form  ECY 010-158

4.   Inspection Requirements

- Site inspection prior to tank removal- NO EXCAVATION is allowed until approved by Tacoma Fire Department

- Site inspection after decommissioning

- Site inspection after removal

- Schedule inspection 48 hours in advance

# Requirements

Tanks located in the South Tacoma Ground Water Protection District:

a.   Notification of the Tacoma Pierce County Health Department at least 60 days in advance of     
      any closing.  253.798.6429, tpchd.org/STGPD

b.   Permanently remove the tank unless the tank is located under a permanent building and 
      cannot be removed without removing the building.

Tanks outside the boundaries of the South Tacoma Ground Water Protection District:

Removal vs. Abandonment in Place

Both removal and abandonment in place are methods of decommissioning available for underground tanks, however, removal of the tank is strongly recommended.

Applicants should carefully review the merits of their options before choosing a method of decommissioning. Tanks suspected of leaking should be removed from the ground rather than abandoned in place. The Tacoma Fire Department cannot predict what future regulations may require of tanks abandoned in place under the current guidelines. A tank abandoned in place now may later require removal at additional cost and potential hazard.

Removal:

- Two 40BC rated fire extinguishers are to be on site within 50 feet of operation

- Rope or ribbon barricades must be provided circling a minimum of 10 feet from operation if yard is not fully fenced

- No smoking signs must be posted in visible locations

- A certificate provided by an ICC UST certified decommissioner verifying that the tank has been properly inerted or is otherwise certified “Safe for Hot Work” shall be issued and available on site for inspection for each underground and aboveground tank being removed regardless of the product previously contained.

1.  The tanks' atmosphere must be inert using one of the following approved methods:

- Dry ice (pellets or chunks of solid CO2). Minimum 30 lbs per 1000 gallons of air space is recommended.

- Compressed CO2 gas in cylinders (Note: This method may only be performed by a Certified Marine Chemist).

- Purging with air (gas-freeing) using Venturi tube apparatus, with proper bonding and grounding and after the tank has been pumped and rinsed by an approved company.

- No cutting or welding allowed unless tanks are certified gas free.

- A separate Fire Prevention Bureau permit is required for cutting and welding operations.

Abandoned in Place:

- Flammable and combustible liquids shall be removed from the tank and connecting piping

- The suction, inlet, gauge, vapor return, and vapor lines shall be disconnected

- Tanks shall be filled completely with an approved inert solid material

- Remaining underground piping shall be capped or plugged

- A record of tank size, location, and date of abandonment shall be retained

- For tanks being decommissioned in place that previously contained Class I liquids a            Certified Marine Chemist certificate must be issued and available on site for inspection certifying that the tank has been properly inerted prior to filling.

- No tanks shall be filled prior to inspection by Tacoma Fire Department

h.   Tanks being decommissioned in place must be filled with a lean concrete mixture. Filling       
      with foam is prohibited